Dome Vent Maintenance

- Periodically check that fans are spinning and that there is some airflow exhausting from the hoods.

- Check for damaged taped seams – reseal if necessary

- Check wiring integrity

- Check for loosened screws or breakage in any of the solar panel assemblies

Changing motors

- Remove 3-4 screws that hold the hood exhaust assembly from the main box structure.

- Check to see if fan is disconnected from motor shaft and if motor is still spinning with sun light hitting the solar panels.

- Remove 4 sheet metal screws that secure the fan bracket to the box.

- Remove zip ties that tie down the wires.

- Cut wires close to the terminal lug on the motor housing

- Take notice that the Grn/Wht wire pair go to the positive side of the motor

- Remove the 2 long screws that secure the motor onto the bracket – spacer washers may fall out as you take out the screws

- Solder on 18 gauge or larger wires to the new motor terminals

- Crimp an in-line connector to existing wiring

- Note:  be careful not to short out the wires that come from the solar panels – if the sun is fully shining on them – there could be 11 volts at 1 amp present.

- Reseal connections with marine grade RTV

- Also – take note on how the seams were all sealed with RTV on the old motors